## Sheet1
PROCESS WATER TANK - REPAIRS & ENHANCEMENT | [7 empty] | Price 1 | Price 2 | Price 3
| S.No |  | Actions | Units | Tank A Quantity | Tank B Quantity | TOTAL QUANTITY | Warranty of 3years | Warranty of 5years | Warranty of 7years
External Repairs | 1 |  | Interlock & Kerbstone removal, Excavation for Crack repair (Tank B - OQ side wall portion) - Upto 2.0m depth | Rmt(Aprox) | 0 | 40 | 40
| 2 |  | Repair External cracks and leakages by injecting appropriate repair compounds. | Rmt(Aprox) | 100 | 200 | 300
| 3 |  | Damaged concrete surface preparation by Grinding to remove loose concrete & repair of Spalled concrete and restoration of surface Integrity. | SqM | 10 | 30 | 40
| 4 |  | Below Ground level Bitumen Water proofing layer rectification (After Crack injection/leak repair) | SqM | 0 | 10 | 10
| 5 |  | After External repair work, Backfilling, Sand bedding & Interlock and kerbstone re installation work. | Rmt(Aprox) | 0 | 40 | 40
Expansion & Construction Joint Rectification | 6 |  | Existing Expansion/Construction Joint Removal and Enhancement/Rectification with Expansion/Construction Joint Sysytem
| Option 01 (Full Replacment+Termination) | a | Existing GRP Layer Removal upto 500mm width on both side of Expansion & construction Joint for damage rectification in the Tank floor | Rmt (Aprox) | 500 | 500 | 1000
|  | b | Existing Expansion joint system removal and replacment with new Expansion Joint system. (Incl. Floor, wall & column portion for both tank) | Rmt (Aprox) | 335 | 335 | 670
|  | c | Existing Construction joint system removal and replacment with new Construction Joint system. (Incl. Floor, wall & column portion for both tank) | Rmt (Aprox) | 455 | 455 | 910
|  | d | Removed GRP layer rectification with proper termination | Rmt (Aprox) | 500 | 500 | 1000
| Option 02 (Only Replacment) | a | Existing Expansion joint system removal and replacment with new Expansion Joint system. (Incl. Floor, wall & column portion for both tank) | Rmt (Aprox) | 335 | 335 | 670
|  | b | Existing Construction joint system removal and replacment with new Construction Joint system. (Incl. Floor, wall & column portion for both tank) | Rmt (Aprox) | 455 | 455 | 910
| Option 03 (Only Wall Portion Repair) | a | Existing damaged Expansion joint system removal and replacment with new Expansion Joint system. (Incl. Wall & column portion for both tank) *Floor Portion not Considered due to GRP Flooring removal leads to future damages | Rmt (Aprox) | 200 | 200 | 400
|  | b | Existing damaged Construction joint system removal and replacment with new Construction Joint system. (Incl. Wall & column portion for both tank) *Floor Portion not Considered due to GRP Flooring removal leads to future damages | Rmt (Aprox) | 100 | 100 | 200
Internal Repairs | 7 |  | Tank Cleaning, Pressure washing and remove complete grit from the tank | Lumpsum |  |  | 1
| 8 |  | Damaged concrete surface preparation by Grinding to remove loose concrete & repair of Spalled concrete and restoration of surface Integrity. | SqM (Aprox) | 10 | 40 | 50
| 9 |  | Repairing the Internal cracks and leakages by injecting appropriate repair compounds. | RM(Aprox) | 50 | 100 | 150
| 10 |  | Surface Preparation and Repair the deteriorated and powdery concrete surface (damaged by stored process water's corrosive nature) using suitable cementitious/epoxy repair material to restore strength and provide a proper base for the cementitious waterproof coating.
| Option 01 (Using Cementitious) | a | For Internal Column (Total Column Area for 2 Tank = 2 Tank x 192 Column x 6.95 Sqm = 2670 Sqm). | SqM (Aprox) | 1335 | 1335 | 2670
|  | b | For Internal Wall (Total Wall Area for 2 Tank = 2 Tank x 1150 Sqm = 2300 Sqm). | SqM (Aprox) | 250 | 1150 | 1400
| Option 02 (Using Epoxy) | a | For Internal Column (Total Column Area for 2 Tank = 2 Tank x 192 Column x 6.95 Sqm = 2670 Sqm). | SqM (Aprox) | 1335 | 1335 | 2670
|  | b | For Internal Wall (Total Wall Area for 2 Tank = 2 Tank x 1150 Sqm = 2300 Sqm). | SqM (Aprox) | 250 | 1150 | 1400
| 11 |  | Surface Preperation and application of Waterproof Protective Coating (Resistant to Process water) for the Column and Wall Area
| Option 01 (Using Cementitious) | a | Internal Column Surface Preparation and Acrylic/Cementitious Based Protective Coating Application (Total Column Area for 2 Tank = 2 Tank x 192 Column x 6.95 Sqm = 2670 Sqm). | SqM (Aprox) | 1335 | 1335 | 2670
|  | b | Internal Wall Area Surface Preparation and Acrylic/Cementitious Based Protective Coating Application (Total Wall Area for 2 Tank = 2 Tank x 1150 Sqm = 2300 Sqm). | SqM (Aprox) | 250 | 1150 | 1400
| Option 02 (Using Epoxy) | a | Internal Column Surface Preparation and Epoxy Based Protective Coating Application (Total Column Area for 2 Tank = 2 Tank x 192 Column x 6.95 Sqm = 2670 Sqm). | SqM (Aprox) | 1335 | 1335 | 2670
|  | b | Internal Wall Area Surface Preparation and Epoxy Based Protective Coating Application (Total Wall Area for 2 Tank = 2 Tank x 1150 Sqm = 2300 Sqm). | SqM (Aprox) | 250 | 1150 | 1400
| 12 |  | Surface Preperation and application of Waterproof Protective Coating (Resistant to Process water) for the Floor Area
| Option 01 (Using Cementitious Enhancement) | a | Existing GRP Lamination Flooring removal (Mechanically/Manually) | Sqm | 2600 | 2600 | 5200
|  | b | Tank Corner (Wall-Floor) Slope Portion Enhancement Work/Additional Protection | RM(Aprox) | 225 | 225 | 450 |  |  |  | Based on Site Condition
|  | c | Surface Preperation, Supply and application of Acrylic/Cementetious water proof Coating | Sqm | 2600 | 2600 | 5200
Note: Expansion Joint Repair Item No 6 (Option 2) Applicable for this Enhancmeent.
| Option 02 (Using Epoxy Enhancement) | a | Existing GRP Lamination Flooring removal (Mechanically/Manually) | Sqm | 2600 | 2600 | 5200
|  | b | Tank Corner (Wall-Floor) Slope Portion Enhancement Work/Additional Protection | RM(Aprox) | 225 | 225 | 450 |  |  |  | Based on Site Condition
|  | c | Surface Preperation, Supply and application of Epoxy water proof Coating | Sqm | 2600 | 2600 | 5200
|  | d | Wall/Column - Floor Coating termination (As per standards) | RM(Aprox) | 500 | 500 | 1000
Note: Expansion Joint Repair Item No 6 (Option 2) Applicable for this Enhancmeent.
| Option 03 (GRP Repair Work) | a | Wall/Column - Floor Coating termination (As per standards) | RM(Aprox) | 500 | 500 | 1000
|  | b | Existing GRP Lamination Flooring Crack portion/Weak point/Damaged portion removal and patchwork with GRP Lamination Work | Sqm(Aprox) | 70 | 30 | 100
Note: Expansion Joint Repair Item No 6 (Option 3) Applicable for this Enhancmeent.
| Option 04 (GRP Repair Work + Additional Coating) | a | Wall/Column - Floor Coating termination (As per standards) | RM(Aprox) | 500 | 500 | 1000
|  | b | Floor Expansion Joint
|  | b | Existing GRP Lamination Flooring Crack portion/Weak point/Damaged portion removal and patchwork with GRP Lamination Work | Sqm(Aprox) | 70 | 30 | 100
|  | c | Surface Preparation and Additional water proof coating application with apporpriate coating material (must be bond with GRP) | Sqm(Aprox) | 2600 | 2600 | 5200
Note: Expansion Joint Repair Item No 6 (Option 1) Applicable for this Enhancmeent.
Other Site Requirements | 13 |  | Scaffolding arrangement (Internal & External) | Lumpsum |  |  | 1
| 14 |  | Safety arrangements and trainings (scaffolder and inspector, chemical handling, confined space, work at height, hole watcher) | Lumpsum |  |  | 1
| 15 |  | Tank Cleaning Waste Sludge Removal from the Tank & Debris Removal from the site | Lumpsum |  |  | 1
| 16 |  | MATERIAL TRANSPORTATION | Lumpsum |  |  | 1
| 17 |  | MOB & DEMOB | Lumpsum |  |  | 1